## Slide 1: False Alarm Resistant Smoke Detection and Smoke Generator Standardization
International Aircraft Systems Fire Protection Working Group
Matthew Karp
May 8, 2018

## Slide 2: Background
14 CFR 25.858
Cargo or baggage compartment smoke or fire detection systems
§25.858 (a) The detection system must provide a visual indication to the flight crew within one minute after the start of a fire

## Slide 3: Background
AC 25-9A [2]
Smoke Detection, Penetration, and Evacuation Tests and Related Flight Manual Emergency Procedures
Paragraph 10a –Smoke or fire detection systems should provide warning before the fire
Paragraph 10b – The smoke detection test is designed to demonstrate that the smoke detection system installation will detect a smoldering fire producing a small amount of smoke.

## Slide 4: Background
14 CFR 23.858 and AC 25-9A
  The cargo or baggage compartment smoke detection system should detect a small smoldering fire within one minute
  A “small smoldering fire” is objective

## Slide 5: Demonstration of a Typical Smoldering Fire Producing Small Amount of Smoke
*Increasing smoke
*Flames at 40 seconds

## Slide 6: Objective
  Quantitatively characterize a suitable smoke source for smoke detection certification

## Slide 7: Questions
Does artificial smoke move like real smoke?
Can artificial smoke cause false alarm resistant detectors to alarm?
Does smoke density, smoke particle size and volumetric flow rate correlate to cargo compartment detection time?
Can standardizing smoke generators make smoke detector certification tests more consistent?

## Slide 8: False Alarm Resistant Detector Theory
False alarm resistant smoke detectors can use size discrimination as a means of rejecting nuisances
  Smoke is typically less than 1 µm
  Smoke detector nuisances are typically greater than 1 µm
Particle size by substance [1]

## Slide 9: Smoke Particle Measurement
Material | Smoke Production and Properties D32 ­(optical measurements), µm [2] | Online determination of the refractive index of test fires Dpg ­­(SMPS), µm [3] | Smoke Characterization Project Ds (WPS), µm [4] | U. S. Environmental Protection Agency (ELPI and SMPS data), µm [5]
Douglas Fir (flaming) | 0.47-0.52 |  | 0.040-0.073 | 0.054-0.077
Douglas Fir (smoldering) | 0.75-0.8 |  | 0.136-0.141 | 
Flaming Wood |  | 0.16 |  | 0.046-0.077
Smoldering Wood |  | 0.19 |  | 
Smoldering Cotton |  | 0.17 | 0.086-0.105 | 
Heptane Flaming |  | 0.16 | 0.195-0.199 | 
PVC Smoldering | 0.8-1.1 | 0.135-0.138 |  | 
PVC Flaming | 0.3-0.6 | 0.100-0.132 |  | 
  Measured smoke diameters varies by material, smoking vs smoldering, researcher and particle sizing instrument
Ranges from 46nm to 1100nm
Average is 263nm

## Slide 10: Theory Light Scattering
Mie Scattering Theory governs light scattering by sub-micron particles
The general solution is found through the application of Maxwell’s equation
A simplified approximation of Mie scattering is given by van de Hulst [6]
Where Q is the efficiency factor of scattering
This shows that the scattering intensity is a function of
  n, Refractive index of the particle
  a, radius of the particle
  λ, Wavelength of the incident light

## Slide 11: Theory Blue and IR Light Scattering
Why use blue and infrared light scattering?
  To discriminate between smoke and other airborne particles
  Blue light scatters submicron particles more efficiently than IR light
Chart: Diameter, µm
Maxwell’s Equation plotted using 470nm for Blue and 850nm for IR scattered light, assuming refractive index of 1.5

## Slide 12: Theory Blue and IR Light Scattering
If the percentage of blue signal is greater than 55%, then the average particle size is most likely less than 370nm
Average smoke particle diameter of researched experiments is 263nm
Chart: Diameter, µm
 | 0.55 | 0.55
 | 0 | 100
Maxwell’s Equation plotted using 470nm for Blue and 850nm for IR scattered light, assuming refractive index of 1.5

## Slide 13: Fire Growth
Fire growth (a) typical curve, and (b) idealized parabolic curve [9]
Smoke transport is buoyance driven due to increased temperature
Incubation period
  Period before flaming
  Representative of smoldering fire
  Varies and is difficult to quantify
Established growth
  Representative of growing fire
  Well studied with the given idealized parabolic equation
  Where
    Q= heat release of fire, kW
    = fire growth coefficient, kW/s2
    t= time after ignition, s
    to=effective ignition time, s

## Slide 14: Heat Release Rate
The fire growth coefficient has accepted values for
  Slow fires (thick wood)
  Medium fires (mattresses)
  Fast fires (cardboard box or clothes)
  Ultra fast fires (methanol fire)
Data for smoldering fire is less prevalent
  The length of incubation period varies
Chart: Time, s
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
Slow | 0 | 0.002931 | 0.011724 | 0.026379 | 0.046896 | 0.073275 | 0.10552 | 0.14362 | 0.18758 | 0.23741 | 0.2931 | 0.35465 | 0.42206 | 0.49534 | 0.57448 | 0.65948 | 0.75034 | 0.84706 | 0.94964 | 1.0581 | 1.1724 | 1.2926 | 1.4186 | 1.5505 | 1.6883 | 1.8319 | 1.9814 | 2.1367 | 2.2979 | 2.465 | 2.6379 | 2.8167 | 3.0013 | 3.1919 | 3.3882 | 3.5905 | 3.7986 | 4.0125 | 4.2324 | 4.4581 | 4.6896 | 4.927 | 5.1703 | 5.4194 | 5.6744 | 5.9353 | 6.202 | 6.4746 | 6.753 | 7.0373 | 7.3275 | 7.6235 | 7.9254 | 8.2332 | 8.5468 | 8.8663 | 9.1916 | 9.5228 | 9.8599 | 10.2028
Medium | 0 | 0.01127 | 0.04508 | 0.10143 | 0.18032 | 0.28175 | 0.40572 | 0.55223 | 0.72128 | 0.91287 | 1.127 | 1.3637 | 1.6229 | 1.9046 | 2.2089 | 2.5358 | 2.8851 | 3.257 | 3.6515 | 4.0685 | 4.508 | 4.9701 | 5.4547 | 5.9618 | 6.4915 | 7.0438 | 7.6185 | 8.2158 | 8.8357 | 9.4781 | 10.143 | 10.8305 | 11.5405 | 12.273 | 13.0281 | 13.8057 | 14.6059 | 15.4286 | 16.2739 | 17.1417 | 18.032 | 18.9449 | 19.8803 | 20.8382 | 21.8187 | 22.8218 | 23.8473 | 24.8954 | 25.9661 | 27.0593 | 28.175 | 29.3133 | 30.4741 | 31.6574 | 32.8633 | 34.0918 | 35.3427 | 36.6162 | 37.9123 | 39.2309
Fast | 0 | 0.04689 | 0.18756 | 0.42201 | 0.75024 | 1.1723 | 1.688 | 2.2976 | 3.001 | 3.7981 | 4.689 | 5.6737 | 6.7522 | 7.9244 | 9.1904 | 10.5503 | 12.0038 | 13.5512 | 15.1924 | 16.9273 | 18.756 | 20.6785 | 22.6948 | 24.8048 | 27.0086 | 29.3063 | 31.6976 | 34.1828 | 36.7618 | 39.4345 | 42.201 | 45.0613 | 48.0154 | 51.0632 | 54.2048 | 57.4402 | 60.7694 | 64.1924 | 67.7092 | 71.3197 | 75.024 | 78.8221 | 82.714 | 86.6996 | 90.779 | 94.9523 | 99.2192 | 103.58 | 108.0346 | 112.5829 | 117.225 | 121.9609 | 126.7906 | 131.714 | 136.7312 | 141.8423 | 147.047 | 152.3456 | 157.738 | 163.2241
Ultra Fast | 0 | 0.1878 | 0.7512 | 1.6902 | 3.0048 | 4.695 | 6.7608 | 9.2022 | 12.0192 | 15.2118 | 18.78 | 22.7238 | 27.0432 | 31.7382 | 36.8088 | 42.255 | 48.0768 | 54.2742 | 60.8472 | 67.7958 | 75.12 | 82.8198 | 90.8952 | 99.3462 | 108.1728 | 117.375 | 126.9528 | 136.9062 | 147.2352 | 157.9398 | 169.02 | 180.4758 | 192.3072 | 204.5142 | 217.0968 | 230.055 | 243.3888 | 257.0982 | 271.1832 | 285.6438 | 300.48 | 315.6918 | 331.2792 | 347.2422 | 363.5808 | 380.295 | 397.3848 | 414.8502 | 432.6912 | 450.9078 | 469.5 | 488.4678 | 507.8112 | 527.5302 | 547.6248 | 568.095 | 588.9408 | 610.1622 | 631.7592 | 653.7318
Smoldering Cotton Wick | 0 | 0.00022 | 0.00088 | 0.00198 | 0.00352 | 0.0055 | 0.00792 | 0.01078 | 0.01408 | 0.01782 | 0.022 | 0.02662 | 0.03168 | 0.03718 | 0.04312 | 0.0495 | 0.05632 | 0.06358 | 0.07128 | 0.07942 | 0.088 | 0.09702 | 0.10648 | 0.11638 | 0.12672 | 0.1375 | 0.14872 | 0.16038 | 0.17248 | 0.18502 | 0.198 | 0.21142 | 0.22528 | 0.23958 | 0.25432 | 0.2695 | 0.28512 | 0.30118 | 0.31768 | 0.33462 | 0.352 | 0.36982 | 0.38808 | 0.40678 | 0.42592 | 0.4455 | 0.46552 | 0.48598 | 0.50688 | 0.52822 | 0.55 | 0.57222 | 0.59488 | 0.61798 | 0.64152 | 0.6655 | 0.68992 | 0.71478 | 0.74008 | 0.76582
Fire Type | Fire growth coefficient, kW/s2
Slow, (Thick wood) [9] | 0.002931
Medium, (cotton, polyester mattresses) [9] | 0.01127
Fast, (Cardboard box, clothes) [9] | 0.04689
Ultra Fast, (methanol fire, soft material furniture) [9] | 0.1778
90 Smoldering Cotton Wick [10] | 0.00022
Fire Type | 
Slow, (Thick wood) [9] | 0.002931
Medium, (cotton, polyester mattresses) [9] | 0.01127
Fast, (Cardboard box, clothes) [9] | 0.04689
Ultra Fast, (methanol fire, soft material furniture) [9] | 0.1778
90 Smoldering Cotton Wick [10] | 0.00022
Growth coefficient plotted with time

## Slide 15: Average Heat Release Rate
Average heat release rate
  Find area under curve (total heat release) and divide by time period
  Heater bars in smoke generators supply a steady power output
Fire Type | Average Heat Release Rate (60 seconds), kW
1 Aviator UL Heat Bar | 0.16
90 Smoldering Cotton Wicks [10] | 0.25
4 Aviator UL Heater Bars | 0.64
Slow, (Thick wood) [9] | 3.4
Medium, (cotton, polyester mattresses) [9] | 13.1
Fast, (Cardboard box, clothes) [9] | 54.4
Ultra Fast, (methanol fire, soft material furniture) [9] | 217
Growth coefficient plotted with time
Chart: 
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60
Slow | 0 | 0.002931 | 0.011724 | 0.026379 | 0.046896 | 0.073275 | 0.10552 | 0.14362 | 0.18758 | 0.23741 | 0.2931 | 0.35465 | 0.42206 | 0.49534 | 0.57448 | 0.65948 | 0.75034 | 0.84706 | 0.94964 | 1.0581 | 1.1724 | 1.2926 | 1.4186 | 1.5505 | 1.6883 | 1.8319 | 1.9814 | 2.1367 | 2.2979 | 2.465 | 2.6379 | 2.8167 | 3.0013 | 3.1919 | 3.3882 | 3.5905 | 3.7986 | 4.0125 | 4.2324 | 4.4581 | 4.6896 | 4.927 | 5.1703 | 5.4194 | 5.6744 | 5.9353 | 6.202 | 6.4746 | 6.753 | 7.0373 | 7.3275 | 7.6235 | 7.9254 | 8.2332 | 8.5468 | 8.8663 | 9.1916 | 9.5228 | 9.8599 | 10.2028
1 Heater Bar | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16
4 Heater Bars | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64 | 0.64
Smoldering Cotton Wick | 0 | 0.00022 | 0.00088 | 0.00198 | 0.00352 | 0.0055 | 0.00792 | 0.01078 | 0.01408 | 0.01782 | 0.022 | 0.02662 | 0.03168 | 0.03718 | 0.04312 | 0.0495 | 0.05632 | 0.06358 | 0.07128 | 0.07942 | 0.088 | 0.09702 | 0.10648 | 0.11638 | 0.12672 | 0.1375 | 0.14872 | 0.16038 | 0.17248 | 0.18502 | 0.198 | 0.21142 | 0.22528 | 0.23958 | 0.25432 | 0.2695 | 0.28512 | 0.30118 | 0.31768 | 0.33462 | 0.352 | 0.36982 | 0.38808 | 0.40678 | 0.42592 | 0.4455 | 0.46552 | 0.48598 | 0.50688 | 0.52822 | 0.55 | 0.57222 | 0.59488 | 0.61798 | 0.64152 | 0.6655 | 0.68992 | 0.71478 | 0.74008 | 0.76582

## Slide 16: Aviator UL Smoke Generator
Utilizes a white mineral oil, smoke fluid 135
Utilizes inert gases as a propellant
  Tests were conducted with nitrogen, carbon dioxide and helium
Smoke volume can be varied
  Adjusting the gas pressure using the regulator valve
  The recommended pressure range is between 15 and 50psig
Smoke density can be varied
  Adjusting the smoke density valve
  0 turns being closed
  4 turns being fully opened
  8 turns being the maximum recommended range
Heat Release Rate can be varied
  4 Heater bars at 160W each (640W total)

## Slide 17: Three Test Setups
2’ x 2’ x 3’ open top Plexiglas test chamber
Funnel from smoke generator to a 2.75” diameter exit
Aft cargo compartment of DC-10

## Slide 18: Test Setup 1
2’ x 2’ x 3’ open top Plexiglas test chamber
Optical density meter
  23” between laser and smoke obscuration detector
Kidde Smoke detector
  2” between optical density meter and smoke detector
2”
Kidde Detector
Optical Density Meter
23”
Plexiglas Test Chamber

## Slide 19
Test starts with the smoke density valve open two turns
After three minutes on the generator is turned off for one minute and the valve is open another one full turn
This is repeated until the smoke density valve is open to eight full turns
Chart: Time, s
2
turns
Test Procedure
Test Example

## Slide 20
Chart: Time, s
Opening the smoke density valve
  Increases the smoke density
    The %obscuration increases
    The blue and IR signal increases
  Decreases the particle size
    The %blue signal decreases
Chart: Time, s
Chart: Time, s
Obscuration, Blue + IR Signal and %Blue

## Slide 21
Chart: % Blue
Can | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3372 | 6011 | 6069 | 4742 | 5246 | 5373 | 5338 | 5431 | 5227 | 4970 | 4567 | 4784 | 5030 | 5043 | 4868 | 4758 | 4702 | 4714 | 4701 | 4552 | 4376 | 4134 | 4118 | 4659 | 2842 | 3181 | 2951 | 3409 | 3074 | 3161 | 3307 | 3296 | 2888 | 421 | 46 | 95 | 32 | 10 | 8 | 21 | 30
Powder | 9 | 5 | 8 | 7 | 7 | 7 | 8 | 5 | 6 | 8 | 6 | 7 | 7 | 6 | 117 | 55 | 275 | 494 | 360 | 375 | 766 | 670 | 653 | 642 | 1218 | 1171 | 1118 | 2491 | 2608 | 2161 | 1705 | 1492 | 1513 | 1513 | 1394 | 1522 | 1531 | 1491 | 1632 | 2118 | 2129 | 2049 | 1844 | 1528 | 1505 | 1524 | 1667 | 1676 | 1606 | 1530 | 1590 | 1659 | 1636 | 1576 | 1545 | 1440
Smoke detector nuisances are mostly low in blue and IR signal detection
However false alarms can occur
  Even with less than 55% blue signal
  But only with a high blue and IR signal
    As seen with talc powder and canned smoke
  Rosco 1700 smoke generator is water based
    Smoke particles are similar to other smoke nuisances
Smoke Detector Nuisances

## Slide 22
Real smoke samples have mostly greater than 55% blue detection
  Agrees with the Mie scattering theory
Chart: % Blue
Real Smoke

## Slide 23
The blue and IR signal varies depending on the gas propellant and the pressure
More details to follow…
Chart: % Blue
Aviator UL Variations

## Slide 24
  Most dense smoke
    Very high blue and IR signal
  % Blue signal mostly greater than 55% or have high Blue and IR signal
    % Blue signal mostly greater than 55% is typical of real smoke
Chart: % Blue
Aviator UL Variations 50psig

## Slide 25
Chart: % Blue
Aviator UL Variations 30psig
  Dense smoke
    High blue and IR signal
    Helium shows less dense smoke
  % Blue signal mostly greater than 55% or have high Blue and IR signal
    % Blue signal mostly greater than 55% is typical of real smoke

## Slide 26
Chart: % Blue
Aviator UL Variations 15psig
  Less dense smoke
    Lower blue and IR signal
    Helium shows less dense smoke
  % Blue mostly greater than 40%
    % Blue less than 55% is typical of smoke alarm nuisances

## Slide 27: Conclusions of Test 1
The blue and IR signal can be used to characterize smoke detector nuisances, actual and generator smoke
The smoke generator particle size, smoke density and/or refractive index varies with
  Gas propellant
  Smoke density valve
  Gas propellant regulator pressure
Smoke obscuration is related to the blue and IR signal
Smoke detector nuisances are
  Mostly low in blue and IR signal detection
  Mostly less than 50% blue signal
Real smoke is
  Mostly high in blue and IR signal detection
  Mostly more than 55% blue detection

## Slide 28: Test Setup 2
Funnel from exit of smoke generator to 2.75” vane anemometer
  Measures volumetric flow rate
Optical density meter
  1” from the exit stack
  Measures percent obscuration/ft
Smoke Generator Standardization Apparatus (SGSA)
  6” from the exit stack
  Measures the blue and IR signal
Kidde smoke detector
  10” from the exit stack
Thermocouples
  Measures ambient, inlet and exit temperature
Carbon dioxide and helium were tested using 1 and 4 heater bars (160 and 640W) at various pressures
SGSA
6”
Kidde Detector
10”
Vane Anemometer/
Exit Stack
Optical Density Meter
1”

## Slide 29: SGSA
0.9" High Brightness LED Spot Light, 470nm
0.9" High Brightness LED Spot Light, 850nm
475nm CWL, 50mm Dia. Hard Coated OD 4 25nm Bandpass Filter
850nm CWL, 50mm Dia. Hard Coated OD 4 25nm Bandpass Filter
Two 50mm Diameter x 44mm FL, PCX Condenser Lens
  Ensures scattered light signal is great enough for measurement
Two Blue Enhanced Response, Silicon Detector
  Measures scattered light at a 45° angle
LEDs
Silicon Detectors
45°
Smoke

## Slide 30
Test starts with the smoke density valve open two turns
After three minutes on the generator is turned off for one minute and the valve is open another one full turn
This is repeated until the smoke density valve is open to eight full turns
Chart: Time, s
2
turns
Test Procedure
Test Example

## Slide 31: Smoke Transport
The smoke transport is buoyancy-driven caused by natural convection
  As the exit temperature increases the volumetric flow rate increases
Chart: Time, s
x | 0 | 10000

## Slide 32: Smoke Transport
The smoke transport due to Archimedes’ principle is insignificant
  Using helium as a propellant does not significantly increase the flow rate compared to using carbon dioxide
The smoke transport is buoyancy-driven caused by natural convection
Chart: Temperature, C
| 45 | 47 | 47 | 85 | 80.900000000000006 | 86 | 87
 | 8.3125 | 8.5208 | 8.8264 | 12.9306 | 13 | 12.6458 | 13.5903
 | 8.3125 | 8.5208 | 8.8264 | 12.9306 | 13 | 12.6458 | 13.5903
Chart: Q, ft3/min
| 1 Heater Bar CO2 30psi | 1 Heater Bar He 15psi | 1 Heater Bar He 30psi | 4 Heater Bars CO2 30psi | 4 Heater Bars CO2 50psi | 4 Heater Bars He 15psi | 4 Heater Bars He 50psi
Volumetric Flow Rate, ft3/min | 8.3125 | 8.5208 | 8.8264 | 12.9306 | 13 | 12.6458 | 13.5903
Temperature, C | 45 | 47 | 47 | 85 | 80.9 | 86 | 87

## Slide 33: Obscuration, Blue + IR Signal
The blue and IR signal strength is positively correlated to the percent obscuration per foot
  At above 50%obs/ft the scattered blue light signal becomes saturated
Chart: Optical Density, %obs/ft
Chart: Optical Density, %obs/ft

## Slide 34: Repeatability and Accuracy
  SGSA and the Aviator UL yield repeatable results over multiple testing dates
  SGSA is able to quantitatively characterize smoke particle diameter and smoke density
    Measuring blue (470nm)and IR (850nm) light scattering signal
  It is possible to quantitatively characterize smoke transport
    Measuring volumetric flow rate
    Measuring temperature entering and exiting smoke generator and ambient temperature for thermal buoyance
Chart: %Blue Signal

## Slide 35: Conclusions of Test 2
The smoke transport is buoyancy-driven caused by natural convection
  The smoke transport due to Archimedes’ principle is insignificant
    Using helium will not have a significant effect on volumetric flow rate
Measuring the blue and IR scattered light is possible with easy to acquire equipment
Blue light becomes saturated at greater than ~50% obscuration/foot
Potential changes to smoke standardization testing
  Eliminate converging cone to keep percent obscuration below 50%
  Measure ambient and heater stack temperature to estimate smoke transport

## Slide 36: Test Setup 3 McDonnell Douglas DC-10
Aft Cargo Compartment [4]
Volume- 2000 ± 100 CU FT
Smoke source in forward left corner of forward section (green)
Smoke detection in aft centerline of forward section (red)
Distance is 19.5ft

## Slide 37: Test Setup 3
Kidde smoke detector
  2” from ceiling
SGSA
  6” from ceiling
Optical density meter
  1” above smoke source
Aviator UL
  CO2
  1 and 4 heater bars (160W and 640W)
  15, 30 and 50psi
MPS fire load
  single-wall corrugated cardboard boxes
  18” x 18” x 18”
  filled with 2.5 lb of loosely packed standard weight office paper shredded into strips
Smoke Source
Kidde Smoke Detector
SGSA

## Slide 38: Repeatability
Reproducible test results occurred over multiple testing dates
  More reproducible with higher heat added
  Blue+IR signal and detection time varied with less heat
Chart: 50 psi 4 Heat 8 Turn
15 psi 4 Heat 8 Turn |  |  | 
 | %Blue | Blue+IR | Detection Time, s
Test 1 | 0.47 | 0.18 | 63
Test 2 | 0.53 | 0.18 | 64
50 psi 4 Heat 8 Turn |  |  | 
 | %Blue | Blue+IR | Detection Time, s
Test 1 | 0.53 | 0.57 | 46
Test 2 | 0.52 | 0.57 | 46
50psi 1heat 8 turn |  |  | 
 | %Blue | Blue+IR | Detection Time, s
Test 1 | 0.68 | 0.64 | 73
Test 2 | 0.70 | 0.53 | 69
30 psi 1 Heat 8 Turn |  |  | 
 | %Blue | Blue+IR | Detection Time, s
Test 1 | 0.67 | 0.47 | 70
Test 2 | 0.68 | 0.37 | 92

## Slide 39: Small Scale Large Scale Comparison
The blue and IR signal from small scale test setup 2 (SST2) is representative of the results from large scale testing (LST3)
  The blue and IR signal is representative of smoke obscuration
The restricted exit of the SST2 saturates the blue signal at high output smoke settings
Chart: Blue + IR LST3, Arb U
| 6.0958975025222406E-2 | 7.5205750460005993E-2 | 9.264547840843522E-2 | 0.10655478629688357 | 0.1678984360100661 | 0.17631472422163677 | 0.18229725577710293 | 0.184 | 0.18498765915950222 | 0.25169085097659522
Unsaturation Zone | 1.143 | 1.143 | 1.293 | 1.104 | 1.75 | 2.203 | 2.203 | 2.1135 | 2.781
Blue Saturation Zone | 2.781 | 2.78 | 2.47 | 2.47 | 2.8764 | 2.708 | 2.708 | 2.8764
 | 0 | 10

## Slide 40: Blue and IR Signal Comparison
Opening the smoke density valve significantly increases the blue and IR signal
Increasing the gas pressure significantly increases the blue and IR signal
Large difference of smoke obscuration between smoldering cardboard and cardboard fire
The restricted exit of the SST2 saturates the blue signal at high output smoke settings
Chart: Blue + IR Signal, Arb. U
| 15psi 4heat 4turn | 15psi 4heat 4turn | 30psi 1heat 4 turn | 30psi 4heat 4 turn | 50psi 4heat 4 turn | 15psi 4heat 8 turn | 15psi 4heat 8 turn | Cardboard smolder | 50psi 1heat 4 turn | 15psi 1heat 8 turn | 30psi 4heat 8 turn | 30psi 1heat 8 turn | 30psi 1heat 8 turn | 50psi 1heat 8 turn | 50psi 4heat 8 turn | 50psi 4heat 8 turn | 50psi 1heat 8 turn | Cardboard Fire
LST3 | 0.060959 | 0.075206 | 0.092645 | 0.10655 | 0.1679 | 0.17631 | 0.1823 | 0.184 | 0.18499 | 0.25169 | 0.37058 | 0.37087 | 0.46771 | 0.534 | 0.56675 | 0.56857 | 0.64152 | 0.824
SST2 | 1.143 | 1.143 | 1.293 | 1.104 | 1.75 | 2.203 | 2.203 | 2.1135 | 2.781 | 2.78 | 2.47 | 2.47 | 2.8764 | 2.708 | 2.708 | 2.8764

## Slide 41: Small Scale Large Scale Comparison
The %blue signal from small scale test setup 2 (SST2) is representative of the results from large scale testing (LST3)
  The %blue signal is representative of the smoke particle diameter
Chart: % Blue LST3
| 0.47435968977949816 | 0.52344790550765907 | 0.52486523528207252 | 0.52500000000000002 | 0.53233794372886867 | 0.53400821543507937 | 0.56514631154634842 | 0.64919366232169728 | 0.66900006812524482 | 0.67897423575801219 | 0.68053710336900664 | 0.69917390011671554 | 0.85291927794623268 | 0.85449126602095526 | 0.85831401617107805 | 0.86733594426018989 | 0.87300567843810206 | 0.89752163275385566
 | 0.562 | 0.485 | 0.497 | 0.497 | 0.562 | 0.577 | 0.469 | 0.469 | 0.55885 | 0.5588 | 0.793 | 0.81 | 0.848 | 0.75584 | 0.848 | 0.824

## Slide 42: % Blue Signal Comparison
Opening the smoke density valve significantly decreases the %blue signal
Increasing the heater bars slightly decreases the %blue signal
  Most noticeable when smoke density valve is more open
In theory, if the percent of blue signal is greater than 55%, then the average particle size is most likely less than ~370nm
Chart: % Blue Signal
| 15psi 4heat 8 turn | 30psi 4heat 8 turn | 50psi 4heat 8 turn | Cardboard smolder | 50psi 4heat 8 turn | 15psi 4heat 8 turn | Cardboard Fire | 15psi 1heat 8 turn | 30psi 1heat 8 turn | 30psi 1heat 8 turn | 50psi 1heat 8 turn | 50psi 1heat 8 turn | 50psi 4heat 4 turn | 30psi 4heat 4 turn | 15psi 4heat 4 turn | 50psi 1heat 4 turn | 15psi 4heat 4turn | 30psi 1heat 4 turn
LST3 | 0.47436 | 0.52345 | 0.52487 | 0.525 | 0.53234 | 0.53401 | 0.56515 | 0.64919 | 0.669 | 0.67897 | 0.68054 | 0.69917 | 0.85292 | 0.85449 | 0.85831 | 0.86734 | 0.87301 | 0.89752
SST2 | 0.562 | 0.485 | 0.497 | 0.497 | 0.562 | 0.577 | 0.469 | 0.469 | 0.55885 | 0.5588 | 0.793 | 0.81 | 0.848 | 0.75584 | 0.848 | 0.824

## Slide 43: Smoke Transport
The time is measured
  T1 starts when smoke source measures >10%obs/ft
  T2 ends when SGSA measures >0.05 Blue+IR signal for >2 seconds
To shorten detection time
  Increase heat output
  Increase smoke output
    Increasing propellant pressure
    Opening smoke density valve
Cardboard fire has the quickest detection time
Chart: Time Until Smoke Detected, s
Chart: Detection Time, s
| 15 psi 1 heat 8 turn | 50 psi 1 heat 4 turn | 30 psi 1 heat 4 turn | 30 psi 1 heat 8 turn | 50 psi 1 heat 8 turn | 30 psi 4 heat 4 turn | 30 psi 1 heat 8 turn | 50 psi 1 heat 8 turn | 50 psi 4 heat 4 turn | 15 psi 4 heat 8 turn | 15 psi 4 heat 8 turn | 30 psi 4 heat 8 turn | cardboard smolder | 50 psi 4 heat 8 turn | 50 psi 4 heat 8 turn | cardboard fire
 | 105 | 102 | 99 | 92 | 73 | 71 | 70 | 69 | 68 | 64 | 63 | 62 | 57 | 46 | 46 | 23
Note: False alarm resistant detectors depend on both the blue+IR signal and the percentage of blue signal, this data depends only on the blue+IR signal
<60 second detection time

## Slide 44: Smoke Transport
Detection time formula (DT)
Where
  BIR is Blue + IR signal, dimensionless
  Q is volumetric flow rate, ft3/s
  V is volume of cargo compartment, ft3
  %B is % Blue signal, dimensionless
  K is constant
To shorten detection time
  Increase heat output, Q
  Increase smoke output, BIR
    Increasing propellant pressure
    Opening smoke density valve
Chart: Time Until Smoke Detected, s
Chart: Detection Time, s
| 105 | 63 | 64 | 99 | 70 | 92 | 71 | 62 | 102 | 73 | 69 | 68 | 46 | 46
 | 68.4002 | 38.721 | 38.721 | 105.331 | 53.5691 | 53.5691 | 61.961 | 31.3463 | 56.2411 | 65.6599 | 65.6534 | 59.8132 | 32.2504 | 32.2504

## Slide 45: Large Scale Test Results
 | %Blue | Blue+IR | Time to Detection
Cardboard Fire | 0.57 | 0.82 | 23
50psi 4 heat 8 turn | 0.53 | 0.57 | 46
50psi 4 heat 8 turn | 0.52 | 0.57 | 46
Cardboard Smolder | 0.53 | 0.18 | 57
30psi 4 heat 8 turn | 0.52 | 0.37 | 62
15psi 4 heat 8 turn | 0.47 | 0.18 | 63
15psi 4 heat 8 turn | 0.53 | 0.18 | 64
50psi 4 heat 4 turn | 0.85 | 0.17 | 68
50psi 1 heat 8 turn | 0.70 | 0.53 | 69
30psi 1 heat 8 turn | 0.67 | 0.47 | 70
30psi 4 heat 4 turn | 0.85 | 0.11 | 71
50psi 1 heat 8 turn | 0.68 | 0.64 | 73
30psi 1 heat 8 turn | 0.68 | 0.37 | 92
30psi 1 heat 4 turn | 0.90 | 0.09 | 99
50psi 1 heat 4 turn | 0.87 | 0.18 | 102
15psi 1 heat 8 turn | 0.65 | 0.25 | 105
Cardboard fire has high heat, high smoke output with a moderate to small sized smoke particle
Smoldering cardboard has moderate heat, low smoke output with a moderate sized smoke particle

## Slide 46: Conclusions of Test 3
Higher heat creates more consistent smoke density and detection time
The blue and IR and the %blue signal from SST2 is representative of the results from LST3
  The restricted exit of the SST2 causes high percent obscuration at high output smoke settings and saturates the blue signal
Detection time is dependent on
  Thermal buoyance
    Volumetric flow rate
    Ambient and exit stack temperature
  Smoke density and particle size
    Blue signal, IR signal and the percentage of blue signal
  Volume of test compartment

## Slide 47: Questions and Answers
Does artificial smoke move like real smoke?
  The transport of artificial smoke can be adjusted by the addition or removal of heat
Can artificial smoke cause false alarm resistant detectors to alarm?
  The quantity and particle size of artificial smoke can be adjusted by manipulating the propellant gas pressure and adjusting the smoke density valve
Does smoke density, smoke particle size and volumetric flow rate correlate to cargo compartment detection time?
  Small scale testing of smoke density, particle size and volumetric flow rate show a direct correlation to large scale testing
  These parameters appear to have a correlation to cargo compartment detection time
Can using a smoke generator standard make smoke detector certification tests more consistent?
  Smoke generators are capable of creating reproducible smoke for smoke detector certification testing

## Slide 48: Moving Forward
  Determine an appropriate average heat release rate
    Quantitatively characterized by volumetric flow rate, power output of heaters and or temperature measurements
  Determine an appropriate amount of smoke
    Quantitatively characterized by blue and IR signal or percent obscuration
  Determine an appropriate particle size
    Quantitatively characterized by percent blue signal
    Possible SMPS testing to verify results of light scattering
Heat Release Rate over Time [9]

## Slide 49: References
[1] Siemens. Aspirating Smoke Detection. Aspirating Smoke Detection, 2015.
[2] Mulholland, G., 2002. Smoke Production and Properties, in “SFPE Handbook of Fire Protection Engineering”, 3rded. Society of Fire Protection Engineers, Boston, pp. 2-258.
[3] eller, Alejandro & Loepfe, Markus & Nebiker, P & Pleisch, R & Burtscher, Heinz. (2006). On-line determination of the optical properties of particles produced by test fires. Fire Safety Journal. 44. 266–273. 10.1016/j.firesaf.2005.10.001.
[4] Newman J.S., Yee G.G., Su P. (2016) Smoke Characterization and Damage Potentials. In: Hurley M.J. et al. (eds) SFPE Handbook of Fire Protection Engineering. Springer, New York, NY
[5] KINSEY, J. S., P. KARIHER, AND Y. DONG. Evaluation of Methods for Physical Characterization of the Fine Particle Emissions from Two Residential Wood Combustion Appliances. ATMOSPHERIC ENVIRONMENT. Elsevier Science Ltd, New York, NY, 43(32):4959-4967, (2009).
[6] van de Hulst, H. C. (1957). Light scattering by small particles. New York: John Wiley and Sons. ISBN 9780486139753.
[7] SmokeCheck 25S (Smoke Alarm Tester) Safety Data Sheet. “According to the Hazard Communication Standard (CFR29 1910.1200) HazCom 2012.” 17 Mar. 2015.
[8] Emami, T. (2017). CHARACTERIZATION OF SMOKE GENERATORS IN TESTING AIRCRAFT SMOKE DETECTORS (Unpublished master's thesis). Rutgers, The State University of New Jersey.
[9] Klote, J. Method of predicting smoke movement in atria with application to smoke management
[10] Li, H. (2013) The determination of the heat release rate on cotton smoldering fire and polyurethane fire

## Slide 50: Contact Information
Matthew Karp
Email: Matthew.Karp@FAA.gov

## Slide 51: Test Aircraft
Cargo Compartments

## Slide 52: Boeing 737-200
Short to medium range
Twinjet
Narrow-body

## Slide 53: Boeing 737-200
Aft cargo
  Dimension A 21’5” long [1]
Fwd cargo
  Dimension B 14’7” long

## Slide 54: Boeing 737-200
Aft Cargo Compartment [1] | Forward Cargo Compartment | Total Bulk Cargo
370 CU FT | 370 CU FT | 740 CU FT

## Slide 55: Boeing 747 SP
Short to ultra long range [2]
Four-engine
Wide-body

## Slide 56: Boeing 747-SP
Aft Cargo Compartment [2] | Forward Cargo Compartment
2150 CU FT | 1750 CU FT

## Slide 57: Boeing 727-100 C
Short to medium range [3]
Trijet
Narrow-body

## Slide 58: Boeing 727-100 C
 | Aft Cargo Compartment [3] | Forward Cargo Compartment
Volume | 470 CU FT | 420 CU FT
Length | 214” | 199”

## Slide 59: McDonnell Douglas DC-10
Medium to long range
Trijet
Wide-body

## Slide 60: McDonnell Douglas DC-10
Forward Cargo Compartment [4]
Volume- 2000 ± 100 CU FT
Leakage Rate- 50±5 CU FT/min

## Slide 61: Summary
Airplane | Aft Cargo Compartment, CU FT | Fwd Cargo Compartment, CU FT
737-200 | 370 | 370
747-SP | 2150 | 1750
727-100 C | 470 | 420
DC-10 | NA | 2000

## Slide 62: References
[1] 737 Airplane Characteristics for Airport Planning, D6-58325-6. 737 Airplane Characteristics for Airport Planning, D6-58325-6, Boeing, 2013.
[2] 747 Airplane Characteristics Airport Planning, D6-58326. 747 Airplane Characteristics Airport Planning, D6-58326, Boeing, 2011.
[3] 727 Airplane Characteristics Airport Planning, D6-58326. 747 Airplane Characteristics Airport Planning, D6-58324, Boeing, 2011.
[4] Reinhardt, J.W., Blake D., and Marker, T., “Development of a Minimum Performance Standard for Aircraft Cargo Compartment Gaseous Fire Suppression Systems,” FAA report DOT/FAA/AR-00/28, September 2000.